## Sheet1
3. COIL STATUS
Address | Legend | Type | Description [KTS-300] | Remark
00001 | Start / Stop State | Digital | 0(OFF), 1(ON) | READ ONLY
00002 | Fault & Alarm Reset Command | Digital | 0(OFF), 1(ON)
00003 | Load Command for Command | Digital | 0(OFF), 1(ON)
00004 | Unload Command for Command | Digital | 0(OFF), 1(ON)
00005 |  | Digital | 0(OFF), 1(ON)
00006 |  | Digital | 0(OFF), 1(ON)
00007 | Serial Start/Stop Command | Digital | 0(STOP), 1(START)
00008 |  | Digital | 0(OFF), 1(ON)
4 / 13
KTS-300
Protocol Reference
4. INPUT STATUS - DIGITAL INPUT PORT
Address | Legend | Type | Description [KTS-300] | Remark
10001 | Emergency Stop S/W Signal | Digital | 0(FAULT)
10002 | #1 Fan Motor Trip Signal | Digital | 0(FAULT)
10003 | #1 Main Motor Trip Signla | Digital | 0(FAULT)
10004 | #2 Fan Motor Trip Signal | Digital | 0(FAULT)
10005 | #2 Main Motor Trip Signla | Digital | 0(FAULT)
10006 | Reverse Phase | Digital | 0(FAULT)
10007 |  | Digital
10008 |  | Digital
10009 |  | Digital
10010 | Remote Start/Stop Signal | Digital | 1(START)
5. INPUT STATUS - DIGITAL OUTPUT PORT
Address | Legend | Type | Description [KTS-300] | Remark
10017 | #1 Main M/C on/off Signal | Digital | 1(ON)
10018 | #1 Star M/C on/off Signal | Digital | 1(ON)
10019 | #1 Delta M/C on/off Signal | Digital | 1(ON)
10020 | #1 Load Solenoid on/off Signal | Digital | 1(ON)
10021 | #2 Main M/C on/off Signal | Digital | 1(ON)
10022 | #2 Star M/C on/off Signal | Digital | 1(ON)
10023 | #2 Delta M/C on/off Signal | Digital | 1(ON)
10024 | #2 Load Solenoid on/off Signal | Digital | 1(ON)
10025 | Multi Function Control N9 | Digital | 1(ON)
10026 | Multi Function Control N10 | Digital | 1(ON)
10027 | Multi Function Control N11 | Digital | 1(ON)
10028 | Multi Function Control N12 | Digital | 1(ON)
10029 | Multi Function Control N13 | Digital | 1(ON)
10030 | Multi Function Control N14 | Digital | 1(ON)
10031 | Multi Function Control N15 | Digital | 1(ON)
10032 | Multi Function Control N16 | Digital | 1(ON)
5 / 13
KTS-300
Protocol Reference
6. INPUT STATUS - FAULT STATE
Address | Legend | Type | Description [KTS-300] | Remark
10033 | Emergency Stop | Digital | 1(FAULT)
10034 | #1 Fan Motor O.L | Digital | 1(FAULT)
10035 | #1 Main Motor O.L | Digital | 1(FAULT)
10036 | #2 Fan Motor O.L | Digital | 1(FAULT)
10037 | #2 Main Motor O.L | Digital | 1(FAULT)
10038 | Reverse Phase | Digital | 1(FAULT)
10039 | Discharge Press. High | Digital | 1(FAULT)
10040 | Discharge Temp. High | Digital | 1(FAULT)
10041 | Discharge Press. Sensor Trip | Digital | 1(FAULT)
10042 | #1 Discharge Temp. Sensor Trip | Digital | 1(FAULT)
10043 | #2 Discharge Temp. Sensor Trip | Digital | 1(FAULT)
10044 |  | Digital
10045 |  | Digital
10046 |  | Digital
10047 |  | Digital
10048 |  | Digital
6 / 13
KTS-300
Protocol Reference
7. INPUT STATUS - ALARM STATE
Address | Legend | Type | Description [KTS-300] | Remark
10049 | Discharge Press. High | Digital | 1(ALARM)
10050 | #1 Discharge Temp. High | Digital | 1(ALARM)
10051 | #2 Discharge Temp. High | Digital | 1(ALARM)
10052 | #1 Service Alarm | Digital | 1(ALARM)
10053 | #2 Service Alarm | Digital | 1(ALARM)
10054 |  | Digital
10055 |  | Digital
10056 |  | Digital
10057 |  | Digital
10058 | - | Digital
10059 |  | Digital
10060 |  | Digital
10061 |  | Digital
10062 |  | Digital
10063 |  | Digital
10064 |  | Digital
8. INPUT STATUS - START INHIBIT STATE
Address | Legend | Type | Description [KTS-300] | Remark
10065 | Discharge Temp. Low | Digital | 1(IN HIBIT)
10066 |  | Digital
7 / 13
KTS-300
Protocol Reference
9. INPUT REGISTER - STATUS
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
3 0001 | Digital Input Port | - | Analog | INT16 | -
3 0002 | Digital Output Port | - | Analog | INT16
3 0003 | Fault Data | - | Analog | INT16
3 0004 | Alarm Data | - | Analog | INT16
3 0005 | Starting Inhibit Alarm Data | - | Analog | INT16
3 0006 | RTC(YEAR) | - | Analog | INT16 | 0~1023
3 0007 | RTC(MONTH) | - | Analog | INT16
3 0008 | RTC(DAY) | - | Analog | INT16
3 0009 | RTC(TIME) | - | Analog | INT16
3 0010 | RTC(MINUTE) | - | Analog | INT16
3 0013 |  | - | Analog | INT16 | - | X 10
3 0017 | Discharge Press | bar | Analog | INT16 | - | X 10
3 0018 |  |  | Analog | INT16
3 0019 | #1 Discharge Temp. | °C | Analog | INT16 | -20.0 ~ 200.0 | X 10
3 0020 | #2 Discharge Temp. | °C | Analog | INT16 | -20.0 ~ 200.0 | X 10
8 / 13
KTS-300
Protocol Reference
10. HOLD REGISTER - OPERATION
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0021 | #1 Unload Pressure | bar | Analog | INT16 | 0.2 ~ 15.8
4 0022 | #1 Load Pressure | bar | Analog | INT16 | 0 ~ 15.6
4 0023 | #2 Unload Pressure | bar | Analog | INT16 | 0.4 ~ 15.8
4 0024 | #2 Load Pressure | bar | Analog | INT16 | 0.2 ~ 15.6
4 0025 | Y-D Time | sec | Analog | INT16 | 0 ~ 3600
4 0026 | Auto Stop Delay Time | sec | Analog | INT16 | 1 ~ 3600
4 0027 | Stop Delay Time | sec | Analog | INT16 | 1 ~ 600
4 0028 | Load Delay Time | sec | Analog | INT16 | 0 ~ 600
4 0029 | Blowdown Delay Time | sec | Analog | INT16 | 0 ~ 600
11. HOLD REGISTER - SCHEDULE
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0041 | SUN - Starting Time |  | Analog | INT16
4 0042 | MON - Starting Time |  | Analog | INT16
4 0043 | TUE - Starting Time |  | Analog | INT16
4 0044 | WED - Starting Time |  | Analog | INT16
4 0045 | THU - Starting Time |  | Analog | INT16
4 0046 | FRI - Starting Time |  | Analog | INT16
4 0047 | SAT - Starting Time |  | Analog | INT16 | 08:30 | 8:30
4 0048 | SUN - End Time |  | Analog | INT16 | 18:30 | 18:30
4 0049 | MON - End Time |  | Analog | INT16
4 0050 | TUE - End Time |  | Analog | INT16
4 0051 | WED - End Time |  | Analog | INT16
4 0052 | THU - End Time |  | Analog | INT16
4 0053 | FRI - End Time |  | Analog | INT16
4 0054 | SAT - End Time |  | Analog | INT16
4 0056 | YEAR |  | Analog | INT16
4 0057 | MONTH |  | Analog | INT16
4 0058 | DAY |  | Analog | INT16
4 0059 | DAY OF THE WEEK |  | Analog | INT16
4 0060 | TIME |  | Analog | INT16
4 0061 | MINUTE |  | Analog | INT16
9 / 13
KTS-300
Protocol Reference
12. HOLD REGISTER - MAINTENANCE
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0081 | #1 Service Time | H | Analog | INT16
4 0082 | #2 Service Time | H | Analog | INT16
- 10 / 13 -
СОЛ/RE
KTS-300
Protocol Reference
13. HOLD REGISTER - SHUTDOWN
Address | Legend | Unit | Type | data TyPe | Description [KTS-300] | Description (MMI) | Remark
4 0101 | Discharge Temp. High | ℃ | Analog | INT16 | 30 ~ 130
4 0102 | Discharge Press. High | bar | Analog | INT16 | 1.2 ~ 16 | X 10
14. HOLD REGISTER - ALARM MODE
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0121 | Discharge Temp. High | ℃ | Analog | INT16 | 30 ~ 130
4 0122 | Discharge Press. High | bar | Analog | INT16 | 1.2 ~ 16 | X 10
15. HOLD REGISTER - START INHIBIT
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0141 | Discharge Temp. Low | ℃ | Analog | INT16 | -50 ~ 50
11 / 13
KTS-300
Protocol Reference
16. HOLD REGISTER - COMPRESSOR
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0161 | Starting Command Mode | - | Analog | INT16 | 0(Local) / 1(RS485 Comm.) / 2(Digital) / 3(Schedule)
4 0162 | Initialization Time | sec | Analog | INT16 | 3 ~ 300
4 0163 | Comp. Start Delay | sec | Analog | INT16 | 0 ~ 30
4 0164 |  | sec | Analog | INT16
4 0165 | Load Command Mode | - | Analog | INT16 | 0(Press. Sensor) / 1(Digital)
4 0166 | Auto Restart | - | Analog | INT16 | 0(OFF) / 1(ON)
4 0167 |  | - | Analog | INT16
12 / 13
KTS-300
Protocol Reference
17. HOLD REGISTER - OPERATION INFORMATION
Address | Legend | Unit | Type | data Type | Description [KTS-300] | Description (MMI) | Remark
4 0261 | Total Run Hours | H | Analog | INT16 | 0 ~ 9990
4 0263 | #1 Motor Run Hours | H | Analog | INT16
4 0265 | #2 Motor Run Hours | H | Analog | INT16
4 0267 | #1 Loaded Hours | H | Analog | INT16
4 0269 | #2 Loaded Hours | H | Analog | INT16
13 / 13